## Pump Formulas
Basic Pump Formulas
PSIG | 51.96 | < Enter PSIG
S.G. | 1 | < Enter S.G. of Fluid
TDH | 120.0276 | < TDH Result
TDH | 120 | < Enter TDH
S.G. | 1 | < Enter S.G. of Fluid
PSIG | 51.96 | < PSIG Result
GPM | 1463 | < Enter GPM
TDH | 105 | < Enter TDH
S.G. | 1 | < Enter S.G. of Fluid
P.E. | 72% | < Enter Pump Eff.
M.E. | 95% | < Enter Motor Eff.
BHP | 56.713 | < BHP Result
Sump Volume - Square / Rectangular
Sump #1
Width Ft. | 7 | < Enter Width
Length Ft. | 14 | < Enter Length
Depth Ft | 11 | < Enter Depth
Cubic Ft | 1078
Gallons | 8063.44
Sump #2
Width Ft. | 5 | < Enter Width
Length Ft. | 5 | < Enter Length
Depth Ft | 7 | < Enter Depth
Cubic Ft | 175
Gallons | 1309
Gal Difference of 1-2 | 6754.44
Pump Operating Cost Comparison
Pump # 1
GPM | 1463 | < Enter GPM
TDH | 105 | < Enter TDH
S.G. | 1 | < Enter S.G. of Fluid
P.E. | 82% | < Enter Pump Eff.
M.E. | 95.5% | < Enter Motor Eff.
# HOURS / DAY | 24 | < Enter Hours / Day
# DAYS / YEAR | 365 | < Enter Days / Year
$ / KWH | 0.08 | < Enter Cost / kWH
Yrly Operate Cost | 25897.279 | Yearly Cost Result
Pump # 2
GPM | 1463 | < Enter GPM
TDH | 105 | < Enter TDH
S.G. | 1 | < Enter S.G. of Fluid
P.E. | 87% | < Enter Pump Eff.
M.E. | 95.5% | < Enter Motor Eff.
# HOURS / DAY | 24 | < Enter Hours / Day
# DAYS / YEAR | 365 | < Enter Days / Year
$ / KWH | 0.08 | < Enter Cost / kWH
Yrly Operate Cost | 24408.9297 | Yearly Cost Result
Yrly Saved Pump # 2 | 1488.3494
BHP = GPM x TDH x SG
(3960) / (PE) / (ME)
TDH = PSIG x 2.31
S.G.
PSIG = .433 x TDH x S.G

## Affinity Laws Toolbox 1
Affinity Laws Toolbox
Calculating GPM with RPM Change - Impeller Diameter Constant
Design RPM | 1800
Design Hz | 60
Design GPM | 300
New Hz | 30
New RPM | 900
New GPM | 150
Calculating TDH with RPM Change - Impeller Diameter Constant
Design RPM | 1800
Design Hz | 60
Design TDH | 100
Design PSIG | 43.29
New Hz | 30
New RPM | 900
New TDH | 25 | 4
New PSIG | 10.8225
Calculating BHP with RPM Change - Impeller Diameter Constant
Design RPM | 1800
Motor Eff. | 95%
Design BHP | 50
Design kW | 39.2632
New RPM | 900
Motor Eff. | 95%
New BHP | 6.25 | 8
New kW | 4.9079
BHP Reduction | 43.75
kW Reduction | 34.3553
Annual Operating Hours |  |  | 8400 | Annual Customer Energy Savings | 15872.1316
Annual kW Reduction |  |  | 288584.2105
Customer Power Rate |  |  | 0.055
Energy Calculations
Note on B5: Enter Design RPM
Note on B6: Enter Design Hz
Note on B7: Enter Design GPM
Note on B9: Enter New Hz
Note on B14: Enter Design RPM
Note on B15: Enter Design Hz
Note on B16: Enter Design Head
Note on B19: Enter New Hz
Note on B26: Enter Motor Efficiency
Note on B27: Enter Design BHP
Note on D40: Enter Customer Rate

## Affinity Laws Toolbox 2
Affinity Laws Toolbox
Calculating GPM with Impeller Change - Speed is Constant
Design GPM | 4600
Design Impeller Diameter | 16.75
New Impeller Diameter | 15.5
New GPM | 4256.7164
Calculating TDH with Impeller Change - Speed is Constant
Design TDH | 100
Design PSIG | 43.29
Design Impeller Diameter | 16.75
New Impeller Diameter | 15.5
New TDH | 85.6315 | 1.1678
New PSIG | 37.0699
Calculating BHP with Impeller Change - Speed is Constant
Design BHP | 340
Motor Efficiency | 96%
Design kW | 264.2083
Design Impeller Diameter | 16.75
New Impeller Diameter | 15.5
New BHP | 269.4198 | 1.262
Motor Efficiency | 96%
New kW | 209.3617
Note on B5: Enter Design GPM
Note on B6: Enter Impeller Diameter
Note on B7: Enter New Impeller Diameter
Note on B12: Enter Design TDH
Note on B15: Enter Design Impeler Diameter
Note on B16: Enter New RPM
Note on B22: Enter Design BHP
Note on B23: Enter Motor Efficiency
Note on B26: Enter Design Head
Note on B27: Enter New RPM

## Electrical Equations
Electrical Equations
| HP = Horsepower | 60
| m.e. = motor efficiency | 0.95
| Kwin = Kilowatts into machine | 47.1158
| HP = Horsepower (motor) | 60
| m.e. = motor efficiency | 0.95
| HP = Horsepower (fanmotor) | 3
| Kwpackage = Kilowatts of the package | 49.4716
Electrical Equations
| p.f. = power factor | 0.99
| amps | 60
| volts | 460
| KW = Kilowatts | 47.3266
| p.f. = power factor | 0.99
| amps | 50
| volts | 460
| HP = Horsepower | 52.867